## Sheet1
The saving with CQM SR-CT-20 forvxt 360RT cooling tower in court house
E - Evaporating water [Ton / h]
| 226.8 |  | m - Cooling water flow in the system [Ton / hr]
| 360 |  | TR - Cooling tower capacity [TR]
| 1 |  | Cp - Specific heat - [Ton cal / Ton water ºc]
| 35 |  | Ti - inlet cooling water temp [ºc]
| 29.4 |  | To -outlet cooling water temp [ºc]
| 5.6 |  | ∆T - ∆T = Ti - To
| 700 |  | Cooling tower conductivity withuot CQM
| 4500 |  | Cooling tower conductivity with CQM
| 500 |  | Makeup water conductivity µs
| 540 |  | λ evaporating water temp. [Ton Cal / Ton water]
with CQM | withuot CQM
0.294 | 5.88 |  | B - Drainage flow rate [m³/h]
2.352 | 2.352 |  | E - Evaporation flow rate [m³/h]
9 | 1.4 |  | C - Concentration cycle
| 4000 |  | Cooling tower working hours per year [h]
| 2.5 |  | Cost of one cubic water $
| 0.5 |  | Cost of chemical treatment to one cubic miter water $
| 55860 |  | The water saving as a result using SRS $
| 16464 |  | The chemical saving as a result using SRS $
| 72324 |  | all the saving $
B = E/ (C-1)